SITE VISIT  REPORT

Project: Alkhidmat Jamal Hospital Renovation & Expansion

Date of Visit: [17/2/2026]

Participants:

- Muhammad Arif khan  (General Secretory South Punjab)

- Ikram Ul Haq Subhani (President Central Punjab AKFP)

- Dr Mohsin 		(District President Khanewal)

- Hammad Akhtar           (Director Operation AKFP)

- Shehrooz                          (Manager Planning and Development department)

- Asad Tufail                       (Manager Diagnostic Network)

EXECUTIVE SUMMARY

A joint site inspection was conducted to evaluate the progress of the ongoing renovation. While structural work is advancing, several critical finishing, electrical, and clinical infrastructure tasks remain outstanding. The following points require immediate attention to meet the operational deadline.

KEY OBSERVATIONS & PENDING WORKS

1. Clinical & Specialized Areas

- Laboratory: Civil and electrical works are currently incomplete; these must be prioritized for equipment installation.

- X-Ray Room: Installation of specialized door is still pending.

- Pharmacy: Construction of storage racks is incomplete.

- Nursing Station: A dedicated station on the First Floor has yet to be established/constructed.

2. Electrical & IT Infrastructure

- Data Networking: No networking sockets were found in any pre-identified areas.

- Power Backup: The UPS line distribution needs to be addressed and routed to the identified critical areas.

3. Civil, Woodwork & Finishing

- Doors & Partitioning:

  - Female Ward: Missing entrance door.

  - Private Rooms: Repair of existing doors is pending; a separation/partition door is also required for the private area corridor.

  - Third Entrance: Door closer installation and marble flooring work remain unfinished.

- Woodwork: General cabinetry and woodwork are lagging across the entire hospital facility.

- Paint & Ceiling:  Final coat of paint is pending in multiple zones.

  - Ceiling panels/surfaces require thorough cleaning of construction dust and debris.

Recommendation:

Relocation of X Ray Room with Laboratory.

CCTV on the first floor.

Small work is required in CSSD area to separate dirty and clean entrance.